## Chiller Eligibility
[12 empty] | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide
Chiller Eligibility Screening Tool 2020
Electric chiller incentives are only available for HVAC space cooling applications. Chillers used for industrial process cooling, ice rinks, data centers and refrigerated warehouses may qualify for a custom incentive (see focusonenergy.com/custom or call 1.800.762.7077).
Please complete all sections highlighted in this color to determine if your chiller is eligible for Focus on Energy incentives.
Chiller Type and Performance Data
Chiller Type:
| Property Type: | Existing Building
| Chiller AHRI Capacity: |  | Tons | enter capacity at AHRI Conditions, not nominal capacity
| AHRI Conditions: | Error - select appropriate Chiller Type
Maximum Chiller Efficiency to Qualify for Focus on Energy Incentives
|  | Path A | Path B
| Full Load Efficiency: |  |  | kW/Ton
| Part Load Efficiency (IPLV): |  |  | kW/Ton
Proposed Chiller Efficiency
Chiller performance data must be at the AHRI conditions listed above
| Known Efficiency Rating: | kW/Ton | [9 empty] | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide
This is equivalent to:
| Full Load Efficiency: |  |  | kW/Ton |  | EER |  | COP
| Part Load Efficiency (IPLV): |  |  | kW/Ton |  | EER |  | COP
If IPLV not known, enter part load ratings below to calculate (otherwise skip)
www.ahrinet.org/App_Content/ahri/files/standards%20pdfs/AHRI%20standards%20pdfs/AHRI%20Standard%20550-590%20(I-P)-2011.pdf
| Known % Load values are: | Tons and Total kW |  | Clear cells C36 to D39 after changing this value
| % Load | Tons | Total kW |  | kW/ton | EER | IPLV Formula Coefficient
| 100% | [5 empty] | 0.01
| 75% | [5 empty] | 0.42
| 50% | [5 empty] | 0.45
| 25% | [5 empty] | 0.12
|  |  | (link cell B29 to here, kW/ton or EER as appropriate)----> | Calculated IPLV:
Chiller Eligibility and Incentive
Per HVAC/Plumbing Incentive Requirements for Chillers, all kW/ton values should be rounded to three decimal places. This is reflected below.
Chiller Type:
|  | Base Incentive Rate: |  | /ton
|  | Additional Incentive Rate: |  | /ton
Max kW/Ton to Qualify
|  | Actual kW/Ton (Rounded to three Decimals) | Path A |  | Path B
| Full Load Efficiency: | 0 |  | Must select a chiller type first! |  | Must select a chiller type first!
| Part Load Efficiency (IPLV): | 0 |  | Must select a chiller type first! |  | Must select a chiller type first!
|  |  | Blank |  | Blank
|  | Eligible? | Error - No Chiller Type Selected |  | Error - No Chiller Type Selected
|  | Incentive Rate ($/ton): | 0 |  | 0
|  | Chiller Capacity (tons): | 0 |  | 0
|  | Total Incentive: | 0 |  | 0
Measure Code
HVAC / PLUMBING INCENTIVE CATALOG - SUPPLEMENTAL DATA SHEET INPUTS | [8 empty] | Path A
Copy the information below onto the supplemental data sheet when submitting your incentive application, or submit the Cooling Eligibility Screening Tool itself. | [8 empty] | Path B
B1 |  | CHILLERS (BUILDING COOLING LOAD) -
INCENTIVE CODE: H2249, H2250, H2251, H2252 , M-H2249, M-H2250, M-H2251, M-H2252
EQUIP # |  | ANNUAL HOURS OF CHILLER OPERATION (hours chiller enabled to provide some cooling to building) |  |  | BUILDING / SPACE DESIGN COOLING LOAD (tons) |  |  | BASE OR TRIM CHILLER?
1
B1 | CHILLERS (BUILDING COOLING LOAD) - | [8 empty] | PAGE 27-29
INCENTIVE CODE: H4712, H4713, H4714, H4715, H4716, H4717, H4718, H4719, H4720, H4721, H4722, H4723, H4724, H4725, H4726, H4727, H4728, H4729, H4730, H4731, H4732, H4733, H4734, H4735
EQUIP # |  |  | BUILDING / SPACE DESIGN COOLING LOAD (tons) |  | BASE OR TRIM CHILLER? |  | CHILLER LOCKOUT TEMPERATURE (°F) |  | CODE COMPLIANCE PATH: A OR B
Example: CH-1 |  |  | 90 |  | Base |  | 53 °F |  | Path A
B2 | CHILLERS (EQUIPMENT PERFORMANCE) - | [8 empty] | PAGE 27-29
INCENTIVE CODE: H4712, H4713, H4714, H4715, H4716, H4717, H4718, H4719, H4720, H4721, H4722, H4723, H4724, H4725, H4726, H4727, H4728, H4729, H4730, H4731, H4732, H4733, H4734, H4735
EQUIP # | (A) AHRI RATED CAPACITY (tons, 3 decimals) | (B) MAX FULL LOAD (kW/ton) (from Measure Description pg 27-29 of catalog) | (C) AHRI RATED FULL LOAD EFFICIENCY (kW/ton, 3 decimals) | (D) MAX PART LOAD (IPLV) (kW/ton) (from Measure Description pg 27-29 of catalog) | (E) AHRI RATED PART LOAD EFFICIENCY (IPLV) (kW/ton, 3 decimals) | (F) DELTA EFFICIENCY: ((B - C) + (D - E)) | (G) ADDITIONAL INCENTIVE ($/ton) | (H) BASE INCENTIVE ($8/ton) | (I) INCENTIVE RATE ($/ton) (G + H) | REQUESTED INCENTIVE* (A x I)
Example: CH-1 | 95 | 1.16 | 1.12 | 0.88 | 0.84 | 0.08 | 10 | 8 | 18 | 1710
CH-1 | [10 empty] | Path A
CH-1 | [10 empty] | Path B
*Focus on Energy may adjust total incentive based on project caps. Please see measure requirements and Terms and Conditions for more information.
[17 empty] | IECC 2015 Code Requirement [from Table C403.2.3(7)] |  | Focus on Energy Min. Efficiency to Qualify |  | Focus on Energy-Existing Building Incentive per Ton |  | Focus on Energy-New Construction Incentive per Ton
[13 empty] | Chiller Type | Min Tons | Max Tons | =1 when matches proposed chiller | Full Load kW/ton | IPLV | Full Load kW/ton | IPLV | Additional per 1.0 kW/ton | Base Incentive | Additional per 1.0 kW/ton | Base Incentive | Measure Code
Path A
[13 empty] | Air-cooled chiller < 150 tons | 0 | 149.99 | 0 | 1.1881 | 0.87591 | 1.16 | 0.88 | 125 | 8 | 90 | 4 | H4712
[13 empty] | Air-cooled chiller ≥ 150 tons | 150 | 1000000 | 0 | 1.1881 | 0.85714 | 1.16 | 0.86 | 125 | 8 | 90 | 4 | H4713
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) < 75 tons | 0 | 74.99 | 0 | 0.75 | 0.6 | 0.72 | 0.6 | 125 | 8 | 90 | 4 | H4716
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 75 tons and < 150 tons | 75 | 149.99 | 0 | 0.72 | 0.56 | 0.69 | 0.56 | 125 | 8 | 90 | 4 | H4717
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 150 tons and < 300 tons | 150 | 299.99 | 0 | 0.66 | 0.54 | 0.63 | 0.54 | 125 | 8 | 90 | 4 | H4718
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 300 tons and < 600 tons | 300 | 599.99 | 0 | 0.61 | 0.52 | 0.58 | 0.52 | 125 | 8 | 90 | 4 | H4719
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 600 tons | 600 | 1000000 | 0 | 0.56 | 0.5 | 0.53 | 0.5 | 125 | 8 | 90 | 4 | H4720
[13 empty] | Water cooled, centrifugal < 150 tons | 0 | 149.99 | 0 | 0.61 | 0.55 | 0.58 | 0.55 | 125 | 8 | 90 | 4 | H4726
[13 empty] | Water cooled, centrifugal ≥ 150 tons and < 300 tons | 150 | 299.99 | 0 | 0.61 | 0.55 | 0.58 | 0.55 | 125 | 8 | 90 | 4 | H4727
[13 empty] | Water cooled, centrifugal ≥ 300 tons and < 400 tons | 300 | 399.99 | 0 | 0.56 | 0.52 | 0.53 | 0.52 | 125 | 8 | 90 | 4 | H4728
[13 empty] | Water cooled, centrifugal ≥ 400 tons and < 600 tons | 400 | 599.99 | 0 | 0.56 | 0.5 | 0.53 | 0.5 | 125 | 8 | 90 | 4 | H4729
[13 empty] | Water cooled, centrifugal ≥ 600 tons | 600 | 1000000 | 0 | 0.56 | 0.5 | 0.53 | 0.5 | 125 | 8 | 90 | 4 | H4730
Path B
[13 empty] | Air-cooled chiller < 150 tons | 0 | 149.99 | 0 | 1.2371 | 0.75949 | 1.24 | 0.73 | 125 | 8 | 90 | 4 | H4714
[13 empty] | Air-cooled chiller ≥ 150 tons | 150 | 1000000 | 0 | 1.2371 | 0.74534 | 1.24 | 0.72 | 125 | 8 | 90 | 4 | H4715
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) < 75 tons | 0 | 74.99 | 0 | 0.78 | 0.5 | 0.78 | 0.47 | 125 | 8 | 90 | 4 | H4721
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 75 tons and < 150 tons | 75 | 149.99 | 0 | 0.75 | 0.49 | 0.75 | 0.46 | 125 | 8 | 90 | 4 | H4722
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 150 tons and < 300 tons | 150 | 299.99 | 0 | 0.68 | 0.44 | 0.68 | 0.41 | 125 | 8 | 90 | 4 | H4723
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 300 tons and < 600 tons | 300 | 599.99 | 0 | 0.625 | 0.41 | 0.625 | 0.38 | 125 | 8 | 90 | 4 | H4724
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 600 tons | 600 | 1000000 | 0 | 0.585 | 0.38 | 0.585 | 0.35 | 125 | 8 | 90 | 4 | H4725
[13 empty] | Water cooled, centrifugal < 150 tons | 0 | 149.99 | 0 | 0.695 | 0.44 | 0.695 | 0.41 | 125 | 8 | 90 | 4 | H4731
[13 empty] | Water cooled, centrifugal ≥ 150 tons and < 300 tons | 150 | 299.99 | 0 | 0.635 | 0.4 | 0.635 | 0.37 | 125 | 8 | 90 | 4 | H4732
[13 empty] | Water cooled, centrifugal ≥ 300 tons and < 400 tons | 300 | 399.99 | 0 | 0.595 | 0.39 | 0.595 | 0.36 | 125 | 8 | 90 | 4 | H4733
[13 empty] | Water cooled, centrifugal ≥ 400 tons and < 600 tons | 400 | 599.99 | 0 | 0.585 | 0.38 | 0.585 | 0.35 | 125 | 8 | 90 | 4 | H4734
[13 empty] | Water cooled, centrifugal ≥ 600 tons | 600 | 1000000 | 0 | 0.585 | 0.38 | 0.585 | 0.35 | 125 | 8 | 90 | 4 | H4735
[13 empty] | kW/ton = 12 / EER | Known Efficiency Rating | Alt rating 1 Units | Alt rating 2 Units | Alt Rating 1 Value Full | Alt Rating 1 Value Part | Alt Rating 2 Value Full | Alt Rating 2 Value Part | Min Efficiency | Max Efficiency
kW/ton = 12 (COP x 3.412)
COP = EER / 3.412
[13 empty] | COP = 12 / (kW/ton) / 3.412 | kW/Ton | EER | COP | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.3 | 1.5
[13 empty] | EER = 12 / kW/ton | EER | kW/Ton | COP | #DIV/0! | #DIV/0! | 0 | 0 | 40 | 8
[13 empty] | EER = COP x 3.412 | COP | kW/Ton | EER | #DIV/0! | #DIV/0! | 0 | 0
Lookup Tables
[12 empty] | Water Cooled Chillers | Air Cooled Chillers | Facility Types |  | Small Biz Eligible Chiller Types |  |  |  |  | Property Type
[12 empty] | 44 deg. F chilled water supply | 44 deg. F chilled water supply | Business |  | Air-cooled chiller < 150 tons |  |  |  |  | Existing Building
[12 empty] | 85 deg. F condenser water entering temp (temp coming back from cooling tower) | 95 deg. F entering air (dry bulb) on the condensing side | Multifamily | M- | Water cooled, positive displacement (rotary screw or scroll) < 75 tons |  |  |  |  | New Construction
[12 empty] | 2.4 gpm/ton flow rate on the chilled water side | 2.4 gpm/ton flow rate on the chilled water side |  |  | Water cooled, positive displacement (rotary screw or scroll) ≥ 75 tons and < 150 tons
[12 empty] | 0.0001 hr ft^2 deg. F/Btu evaporator fouling factor allowance | 0.0001 hr ft^2 deg. F/Btu evaporator fouling factor allowance |  |  | Water cooled, centrifugal < 150 tons
3.0 gpm/ton flow rate on the condenser water side
0.00025 hr ft^2 deg. F/Btu condenser fouling factor allowance
[12 empty] | % Load IPLV Calc Lookups | Column 1 | Column 2
[12 empty] | Tons and Total kW | Tons | Total kW
[12 empty] | kW/Ton | kW/ton
[12 empty] | EER | EER
[12 empty] | Short | Eligibility Details
[12 empty] | Blank | Error - No Chiller Type Selected
[12 empty] | Qualifies | YES, Chiller meets full load and part load efficiency requirements
[12 empty] | DNQ | NO, Chiller does not meet full load or part load efficiency requirements
Successful incentive message
Congratulations! Your chiller qualifies for an incentive. Please use the HVAC/Plumbing Incentive Catalog available at focusonenergy.com/businesshvac to complete your incentive application upon project completion. Chiller incentives require use of the Supplemental Data Sheet along with the application, which should be completed using the inputs shown below.
Note on H36: Zach Obert: From page 9 of: http://www.ahrinet.org/App_Content/ahri/files/standards%20pdfs/AHRI%20standards%20pdfs/AHRI%20Standard%20550-590%20(I-P)-2011.pdf

## RTU & Split System
[9 empty] | hide | hide | hide | hide | hide |  | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide
DX Cooling Eligibility Screening Tool 2020
Incentives are for standard HVAC space cooling applications only, with the exception of AHRI listed equipment < 5.42 tons (65,000 Btu/h) which may be used in data center and telecom facilities. Rooftop units and split system air conditioners ≥ 5.42 tons used for industrial process cooling, ice rinks, data centers and refrigerated warehouses may qualify for a custom incentive (see focusonenergy.com/custom or call 1.800.762.7077).
Please complete all sections highlighted in this color to determine if your DX Cooling project is eligible for Focus on Energy incentives.
DX Cooling Type and Performance Data
Facility Type:
| Property Type: | Existing Building
| AHRI Cooling Capacity (tons): |  | 0 |  | Enter capacity at AHRI Conditions, not nominal capacity
| DX Cooling Type: | Packaged | [11 empty] | text for Data Validation of cell C11...=if(c8=m142,o157:o158,if(c10<=5.42,p157:p159,if(c10>=11.25,aa157:aa159,v157:v158)))
| Number of A/C Units: | 1 | [11 empty] | text for Data Validation of cell C11...=if(Facility Type = Data Center,o157:o158,if(tons<=5.42,p157:p159,if(tons>=11.25,z157:z159,u157:u158)))
| Known Cooling Efficiency Rating: | EER |  |  | Cooling performance data must be at the AHRI conditions
This is equivalent to:
| Full Load Cooling Efficiency: |  | SEER |  |  | kW/Ton | 0 | COP
| Part Load Cooling Efficiency: |  | SEER |  |  | kW/Ton | 0 | COP
| Heating Efficiency (Heat Pump Only): | 9
DX Cooling Eligibility and Incentive
|  | Min to Qualify | Actual Efficiency
| Full Load Cooling Efficiency (SEER): |  | 0 | Must select a DX Cooling Type first!
| Full Load Cooling Efficiency (EER): |  | 0 | Must select a DX Cooling Type first!
| Part Load Cooling Efficiency (IEER): |  | 0 | Must select a DX Cooling Type first!
| Heating Efficiency (HSPF)(Heat Pump Only): |  | N/A | Must select a DX Cooling Type first!
Eligible?
| #N/A | 0 | #N/A
| #N/A | 0
| #N/A | 0
| AHRI Capacity (tons): | 0
| Incentive Each: | #N/A
| Number of A/C Units: | 1
| Total Incentive: | #N/A
Note: Supplemental Data Sheet inputs apply only to larger systems (≥5.42 tons).
Measure Code
Copy the information below onto the supplemental data sheet when submitting your incentive application.
A1 | AIR CONDITIONING SPLIT AND PACKAGED SYSTEMS (≥ 5.42 TONS) - INCENTIVE CODE: H4368, H4369, H4370, H4371 | [6 empty] | PAGE 25
EQUIP # | (A) AHRI RATED CAPACITY (tons, 2 decimals) | (B) AHRI RATED PART LOAD EFFICIENCY (IEER, 2 decimals) | (C) PART LOAD EFF TO QUALIFY (IEER) (from Measure Description pg 25) | (D) DELTA EFFICIENCY (B - C) | (E) ADDITIONAL INCENTIVE (D x $/ton) | (F) BASE INCENTIVE ($/ton) | (G) INCENTIVE RATE ($/ton) (E + F) | REQUESTED INCENTIVE* (A x G)
Example: AC-1 | 1 @ 15.00 tons | 13.6 | 13 | 0.6 | 3 | 25 | 28 | 420
System 1 | 1 @ 0.00 tons | 0 |  | #VALUE! | 0 | #N/A | #N/A | #N/A
*Focus on Energy may adjust total incentive based on project caps. Please see measure requirements and Terms and Conditions for more information.
#N/A | [7 empty] | Measure Code
Copy the information below onto the supplemental data sheet when submitting your incentive application. | [6 empty] | #N/A | #N/A
A2 | SPLIT SYSTEM AIR CONDITIONING - CONDENSING UNIT ONLY - INCENTIVE CODE H3909 | [6 empty] | PAGE 26
EQUIP # | (A) AHRI RATED CAPACITY (tons, 2 decimals) | (B) AHRI RATED FULL LOAD EFFICIENCY (EER, 2 decimals) | (C) FULL LOAD EFF TO QUALIFY (EER) (from Measure Description pg 26) | (D) DELTA EFFICIENCY (B - C) | (E) ADDITIONAL INCENTIVE (D x $/ton) | (F) BASE INCENTIVE ($/ton) | (G) INCENTIVE RATE ($/ton) (E + F) | REQUESTED INCENTIVE* (A x G)
Example: AC-1 | 1 @ 15.00 tons | 11.6 | 11.1 | 0.5 | 2.5 | 20 | 22.5 | 337.5
System 1 | 1 @ 0.00 tons | 0 |  | #VALUE! | 0 | #N/A | #N/A | #N/A
*Focus on Energy may adjust total incentive based on project caps. Please see measure requirements and Terms and Conditions for more information.
Intermediate Calcs
[9 empty] | Size Range: |  | <5.42
[9 empty] | SEER Threshold: |  | 15
[9 empty] | Potential Measure Code: |  | #N/A
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
[9 empty] | Lookup Tables |  |  |  | Focus Min. Efficiency to Qualify |  |  |  | Existing Building Incentive |  |  |  | New Construction Incentive
[9 empty] | Measure Code | Facility Type | DX Cooling Type | Size Range | SEER | EER | IEER | HSPF | Base Incentive | Additional Incentive | Incentive is per… | Supplemental Data Sheet | Base Incentive | Additional Incentive | Incentive is per…
[9 empty] | PS4768 | Data Center and Telecom | Split System | <5.42 | 15 | N/A | N/A | N/A | 150 | 0 | A/C Unit | None | 100 | 0 | A/C Unit
[9 empty] | PS4769 | Data Center and Telecom | Split System | <5.42 | 16 | N/A | N/A | N/A | 200 | 0 | A/C Unit | None | 150 | 0 | A/C Unit
[9 empty] | PS4770 | Data Center and Telecom | Split System | <5.42 | 17 | N/A | N/A | N/A | 250 | 0 | A/C Unit | None | 175 | 0 | A/C Unit
[9 empty] | PS4771 | Data Center and Telecom | Split System | <5.42 | 18 | N/A | N/A | N/A | 300 | 0 | A/C Unit | None | 200 | 0 | A/C Unit
[9 empty] | PS4772 | Data Center and Telecom | Packaged | <5.42 | 15 | N/A | N/A | N/A | 150 | 0 | A/C Unit | None | 75 | 0 | A/C Unit
[9 empty] | PS4773 | Data Center and Telecom | Packaged | <5.42 | 16 | N/A | N/A | N/A | 200 | 0 | A/C Unit | None | 100 | 0 | A/C Unit
[9 empty] | PS4774 | Data Center and Telecom | Packaged | <5.42 | 17 | N/A | N/A | N/A | 250 | 0 | A/C Unit | None | 125 | 0 | A/C Unit
[9 empty] | PS4775 | Data Center and Telecom | Packaged | <5.42 | 18 | N/A | N/A | N/A | 300 | 0 | A/C Unit | None | 150 | 0 | A/C Unit
[9 empty] | H4736 | Business | Split System | <5.42 | 15 | N/A | N/A | N/A | 50 | 0 | A/C Unit | None | 25 | 0 | A/C Unit
[9 empty] | H4737 | Business | Split System | <5.42 | 16 | N/A | N/A | N/A | 75 | 0 | A/C Unit | None | 35 | 0 | A/C Unit
[9 empty] | H4738 | Business | Split System | <5.42 | 17 | N/A | N/A | N/A | 100 | 0 | A/C Unit | None | 50 | 0 | A/C Unit
[9 empty] | H4739 | Business | Split System | <5.42 | 18 | N/A | N/A | N/A | 125 | 0 | A/C Unit | None | 60 | 0 | A/C Unit
[9 empty] | H4740 | Business | Packaged | <5.42 | 15 | N/A | N/A | N/A | 50 | 0 | A/C Unit | None | 25 | 0 | A/C Unit
[9 empty] | H4741 | Business | Packaged | <5.42 | 16 | N/A | N/A | N/A | 75 | 0 | A/C Unit | None | 35 | 0 | A/C Unit
[9 empty] | H4742 | Business | Packaged | <5.42 | 17 | N/A | N/A | N/A | 100 | 0 | A/C Unit | None | 50 | 0 | A/C Unit
[9 empty] | H4743 | Business | Packaged | <5.42 | 18 | N/A | N/A | N/A | 125 | 0 | A/C Unit | None | 60 | 0 | A/C Unit
[9 empty] | H4744 | Business | Heat Pump | <5.42 | 15 | N/A | N/A | 9 | 50 | 0 | A/C Unit | None | 25 | 0 | A/C Unit
[9 empty] | H4745 | Business | Heat Pump | <5.42 | 16 | N/A | N/A | 9 | 75 | 0 | A/C Unit | None | 35 | 0 | A/C Unit
[9 empty] | H4746 | Business | Heat Pump | <5.42 | 17 | N/A | N/A | 9 | 100 | 0 | A/C Unit | None | 50 | 0 | A/C Unit
[9 empty] | H4747 | Business | Heat Pump | <5.42 | 18 | N/A | N/A | 9 | 125 | 0 | A/C Unit | None | 60 | 0 | A/C Unit
[9 empty] | H4368 | Business | Split System | 5.42-11.24 | N/A | 12 | 13.8 | N/A | 25 | 5 | ton | A1 | 20 | 3 | ton | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4368 | Business | Packaged | 5.42-11.24 | N/A | 12 | 13.8 | N/A | 25 | 5 | ton | A1 | 20 | 3 | ton | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4369 | Business | Split System | 11.25-19.99 | N/A | 12 | 13 | N/A | 25 | 5 | ton | A1 | 20 | 3 | ton | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4369 | Business | Packaged | 11.25-19.99 | N/A | 12 | 13 | N/A | 25 | 5 | ton | A1 | 20 | 3 | ton | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4370 | Business | Split System | 20-63.32 | N/A | 10.3 | 12.1 | N/A | 25 | 5 | ton | A1 | 20 | 3 | ton | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4370 | Business | Packaged | 20-63.32 | N/A | 10.3 | 12.1 | N/A | 25 | 5 | ton | A1 | 20 | 3 | ton | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4371 | Business | Split System | >=63.33 | N/A | 9.7 | 11.4 | N/A | 25 | 5 | ton | A1 | 20 | 3 | ton | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4371 | Business | Packaged | >=63.33 | N/A | 9.7 | 11.4 | N/A | 25 | 5 | ton | A1 | 20 | 3 | ton | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H3909 | Business | Condensing Unit Only | >=11.25 | N/A | 11.1 | N/A | N/A | 20 | 5 | ton | A2 | 15 | 3 | ton | Additional incentive is per ton for each 1.0 EER over baseline
Property Type
Existing Building
New Construction
[9 empty] | Facility Types |  | Additional Incentive On:
[9 empty] | Business |  | Split System | IEER
[9 empty] | Data Center and Telecom |  | Packaged | IEER
[11 empty] | Condensing Unit Only | EER
[9 empty] | Efficiency Units Conversion |  |  | Full Load |  |  |  | Part Load
[9 empty] | kW/ton = 12 / EER |  | Known Efficiency Rating | Alt Rating 1 |  | Alt Rating 2 |  | Alt Rating 1 |  | Alt Rating 2
[9 empty] | kW/ton = 12 (COP x 3.412) |  | kW/Ton | #DIV/0! | EER | #DIV/0! | COP | #DIV/0! | EER | #DIV/0! | COP
[9 empty] | COP = EER / 3.412 |  | EER | #DIV/0! | kW/Ton | 0 | COP | #DIV/0! | kW/Ton | 0 | COP
[9 empty] | COP = 12 / (kW/ton) / 3.412 |  | COP | #DIV/0! | kW/Ton | 0 | EER | #DIV/0! | kW/Ton | 0 | EER
[9 empty] | EER = 12 / kW/ton |  | SEER | #DIV/0! | kW/Ton | 0 | COP | #DIV/0! | kW/Ton | 0 | COP
EER = COP x 3.412
System Types
[9 empty] | Program & Size: |  | Data Center, <= tons | Business, <5.42 tons | [5 empty] | Business, 5.42-11.25 tons |  |  |  |  | Business, >11.25 tons
[11 empty] | Split System | Split System | [5 empty] | Split System |  |  |  |  | Split System
[11 empty] | Packaged | Packaged | [5 empty] | Packaged |  |  |  |  | Packaged
[12 empty] | Heat Pump | [10 empty] | Condensing Unit Only
Successful incentive message
Congratulations! Your DX Cooling project qualifies for an incentive. Please use the HVAC/Plumbing Incentive Catalog available at focusonenergy.com/businesshvac to complete you incentive application upon project completion. DX Cooling incentives require use of the Supplemental Data Sheet along with the application, which should be completed using the inputs shown below.
Congratulations! Your DX Cooling project qualifies for an incentive. Please use the HVAC/Plumbing Incentive Catalog available at focusonenergy.com/businesshvac to complete you incentive application upon project completion.
Congratulations! Your Data Center and Telecom Cooling Equipment project qualifies for an incentive. Please use the Process Systems Incentive Catalog available at focusonenergy.com/applications to complete you incentive application upon project completion.
Supplemental Data Sheet Needed Text
THIS SUPPLEMENTAL DATA SHEET NOT NEEDED FOR THIS FACILITY TYPE & A/C SIZE
HVAC / PLUMBING INCENTIVE CATALOG - SUPPLEMENTAL DATA SHEET INPUTS

## Setup (hidden)
Tons # of decimals: | 0