## Chiller Eligibility
[11 empty] | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide
Chiller Eligibility Screening Tool 2016
Incentives for chillers are not available for Large Energy Users Program customers, regardless of results of this eligibility tool. To check if you are a Large Energy Users Program customer, call 800.762.7077.
Please complete all sections highlighted in this color to determine if your chiller is eligible for Focus on Energy incentives.
Chiller Type and Performance Data
Chiller Type:
| Chiller AHRI Capacity: |  | Tons | enter capacity at AHRI Conditions, not nominal capacity
| Facility Type: | Business
| AHRI Conditions: | Error - select appropriate Chiller Type
Maximum Chiller Efficiency to Qualify for Focus on Energy Incentives
| Full Load Efficiency: |  | kW/Ton
| Part Load Efficiency (IPLV): |  | kW/Ton
Proposed Chiller Efficiency
Chiller performance data must be at the AHRI conditions listed above
| Known Efficiency Rating: | kW/Ton
This is equivalent to:
| Full Load Efficiency: |  | kW/Ton |  |  | EER |  | COP
| Part Load Efficiency (IPLV): |  | kW/Ton |  |  | EER |  | COP
If IPLV not known, enter part load ratings below to calculate (otherwise skip)
www.ahrinet.org/App_Content/ahri/files/standards%20pdfs/AHRI%20standards%20pdfs/AHRI%20Standard%20550-590%20(I-P)-2011.pdf
| Known % Load values are: | Tons and Total kW |  | Clear cells B31 to C34 after changing this value
| % Load | Tons | Total kW |  | kW/ton | EER | IPLV Formula Coefficient
| 100% | [5 empty] | 0.01
| 75% | [5 empty] | 0.42
| 50% | [5 empty] | 0.45
| 25% | [5 empty] | 0.12
|  | (link cell B26 to here, kW/ton or EER as appropriate)----> |  | Calculated IPLV:
Chiller Eligibility and Incentive
Chiller Type:
|  | Max kW/Ton to Qualify | Actual kW/Ton
| Full Load Efficiency: |  | 0 |  | Must select a chiller type first!
| Part Load Efficiency (IPLV): |  | 0 |  | Must select a chiller type first!
Blank
| Eligible? | Error - No Chiller Type Selected
| Incentive Rate ($/ton): | 0
| Chiller Capacity (tons): | 0
| Total Incentive: | 0
HVAC / PLUMBING INCENTIVE CATALOG - SUPPLEMENTAL DATA SHEET INPUTS | [8 empty] | Measure Code
Copy the information below onto the supplemental data sheet when submitting your incentive application.
B1 |  | CHILLERS (BUILDING COOLING LOAD) -
INCENTIVE CODE: H2249, H2250, H2251, H2252 , M-H2249, M-H2250, M-H2251, M-H2252
EQUIP # |  | MODEL # |  |  | ANNUAL HOURS OF CHILLER OPERATION |  | BUILDING / SPACE DESIGN COOLING LOAD (tons) |  | BASE OR TRIM CHILLER?
1
B2 |  | CHILLERS (BUILDING COOLING LOAD) -
INCENTIVE CODE: H2249, H2250, H2251, H2252 , M-H2249, M-H2250, M-H2251, M-H2252
EQUIP # | AHRI RATED CAPACITY (tons) | MAX FULL LOAD (kW/ton) (from Measure Description pg 28 of catalog) | AHRI RATED FULL LOAD EFFICIENCY (kW/ton) | MAX PART LOAD (IPLV) (kW/ton) (from Measure Description pg 28 of catalog) | AHRI RATED PART LOAD EFFICIENCY (IPLV) (kW/ton) | DELTA EFFICIENCY: (max full load - rated full load) + (max part load - rated part load) | ADDITIONAL INCENTIVE ($/ton) (delta efficiency x $250) | BASE INCENTIVE ($/ton) | INCENTIVE RATE ($/ton) (additional incentive + base incentive) | TOTAL INCENTIVE* (AHRI rated capacity x incentive rate)
1 |  |  | 0 |  | 0 |  |  |  | 0 | 0
*Focus on Energy may adjust total incentive based on project caps. Please see measure requirements and Terms and Conditions for more information.
[16 empty] | ASHRAE 90.1-2007 Code Requirement |  | Focus on Energy Min. Efficiency to Qualify |  | Focus on Energy Incentive per Ton
[12 empty] | Chiller Type | Min Tons | Max Tons | =1 when matches proposed chiller | Full Load kW/ton | IPLV | Full Load kW/ton | IPLV | Additional per 0.1 kW/ton | Base Incentive | Measure Code
[12 empty] | Air-cooled chiller < 150 tons | 0 | 149.9 | 0 | 1.2561 | 1.1531 | 1.2 | 0.9 | 250 | 12 | H2249
[12 empty] | Air-cooled chiller ≥ 150 tons | 150 | 1000000 | 0 | 1.2561 | 1.1531 | 1.2 | 0.9 | 250 | 10 | H2249
[12 empty] | Water cooled, positive displacement < 75 tons | 0 | 74.9 | 0 | 0.79034 | 0.67635 | 0.74 | 0.58 | 250 | 10 | H2250
[12 empty] | Water cooled, positive displacement ≥ 75 tons and < 150 tons | 75 | 149.9 | 0 | 0.79034 | 0.67635 | 0.74 | 0.58 | 250 | 10 | H2250
[12 empty] | Water cooled, positive displacement ≥ 150 tons and < 300 tons | 150 | 299.9 | 0 | 0.71775 | 0.62804 | 0.67 | 0.53 | 250 | 10 | H2252
[12 empty] | Water cooled, positive displacement ≥ 300 tons | 300 | 1000000 | 0 | 0.63945 | 0.57187 | 0.59 | 0.47 | 250 | 10 | H2251
[12 empty] | Water cooled, centrifugal < 150 tons | 0 | 149.9 | 0 | 0.7034 | 0.6699 | 0.65 | 0.57 | 250 | 10 | H2250
[12 empty] | Water cooled, centrifugal ≥ 150 tons and < 300 tons | 150 | 299.9 | 0 | 0.63369 | 0.5961 | 0.58 | 0.5 | 250 | 10 | H2250
[12 empty] | Water cooled, centrifugal ≥ 300 tons and < 600 tons | 300 | 599.9 | 0 | 0.57656 | 0.54953 | 0.53 | 0.45 | 250 | 10 | H2252
[12 empty] | Water cooled, centrifugal ≥ 600 tons | 600 | 1000000 | 0 | 0.57656 | 0.54953 | 0.53 | 0.45 | 250 | 10 | H2251
[12 empty] | kW/ton = 12 / EER | Known Efficiency Rating | Alt rating 1 Units | Alt rating 2 Units | Alt Rating 1 Value Full | Alt Rating 1 Value Part | Alt Rating 2 Value Full | Alt Rating 2 Value Part | Min Efficiency | Max Efficiency
kW/ton = 12 (COP x 3.412)
COP = EER / 3.412
[12 empty] | COP = 12 / (kW/ton) / 3.412 | kW/Ton | EER | COP | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.3 | 1.5
[12 empty] | EER = 12 / kW/ton | EER | kW/Ton | COP | #DIV/0! | #DIV/0! | 0 | 0 | 40 | 8
[12 empty] | EER = COP x 3.412 | COP | kW/Ton | EER | #DIV/0! | #DIV/0! | 0 | 0
Lookup Tables
[11 empty] | Water Cooled Chillers | Air Cooled Chillers
[11 empty] | 44 deg. F chilled water supply | 44 deg. F chilled water supply
[11 empty] | 85 deg. F condenser water entering temp (temp coming back from cooling tower) | 95 deg. F entering air (dry bulb) on the condensing side
[11 empty] | 2.4 gpm/ton flow rate on the chilled water side | 2.4 gpm/ton flow rate on the chilled water side
[11 empty] | 0.0001 hr ft^2 deg. F/Btu evaporator fouling factor allowance | 0.0001 hr ft^2 deg. F/Btu evaporator fouling factor allowance
3.0 gpm/ton flow rate on the condenser water side
0.00025 hr ft^2 deg. F/Btu condenser fouling factor allowance
[11 empty] | % Load IPLV Calc Lookups | Column 1 | Column 2
[11 empty] | Tons and Total kW | Tons | Total kW
[11 empty] | kW/Ton | kW/ton
[11 empty] | EER | EER
[11 empty] | Short | Eligibility Details
[11 empty] | Blank | Error - No Chiller Type Selected
[11 empty] | Both | YES, Chiller meets full load and part load efficiency requirements
[11 empty] | Full | YES, Chiller meets full load efficiency requirement only
[11 empty] | Part | YES, Chiller meets part load efficiency requirement only
[11 empty] | Negative | No, Based on performance data the resulting incentive is negative.
[11 empty] | Neither | NO, Chiller does not meet full load or part load efficiency requirements
Successful incentive message
Congratulations! Your chiller qualifies for an incentive. Please use the HVAC/Plumbing Incentive Catalog available at focusonenergy.com/businesshvac to complete you incentive application upon project completion. Chiller incentives require use of the Supplemental Data Sheet along with the application, which should be completed using the inputs shown below.
Note on H35: Zach Obert: From page 9 of: http://www.ahrinet.org/App_Content/ahri/files/standards%20pdfs/AHRI%20standards%20pdfs/AHRI%20Standard%20550-590%20(I-P)-2011.pdf